## Sheet1
Attack # | Start Time | End Time | Attack Point | Start State | Attack | Actual Change | Expected Impact or attacker intent | Unexpected Outcome
1 | 2015-12-28 10:29 | 2015-12-28 10:45 | MV-101 | MV-101 is closed | Open MV-101 | Yes | Tank overflow
2 | 2015-12-28 10:51 | 2015-12-28 10:58 | P-102 | P-101 is on where as P-102 is off | Turn on P-102 | Yes | Pipe bursts
3 | 2015-12-28 11:22 | 2015-12-28 11:28 | LIT-101 | Water level between L and H | Increase by 1 mm every second | No | Tank Underflow; Damage P-101
4 | 2015-12-28 11:48 | 2015-12-28 11:54 | MV-504 | MV-504 is closed | Open MV-504 | Yes | Halt RO shut down sequence; Reduce life of RO | No impact
6 | 2015-12-28 12:01 | 2015-12-28 12:04 | AIT-202 | Value of AIT-202 is >7.05 | Set value of AIT-202 as 6 | No | P-203 turns off; Change in water quality | Impact seen on AIT-504 after two hours at around 14:15. It increased above HH but Drainage did not start
7 | 2015-12-28 12:08 | 2015-12-28 12:16 | LIT-301 | Water level between L and H | Water level increased above HH | No | Stop of inflow; Tank underflow; Damage P-301
8 | 2015-12-28 13:10 | 2015-12-28 13:26 | DPIT-301 | Value of DPIT is <40kpa | Set value of DPIT as >40kpa | No | Backwash process is started again and again; Normal operation stops; Decrease in water level of tank 401. Increase in water level of tank 301
10 | 2015-12-28 14:16 | 2015-12-28 14:19 | FIT-401 | Value of FIT-401 above 1 | Set value of FIT-401 as <0.7 | No | UV shutdown; P-501 turns off; | UV did not shutdown; P-501 did not turn off
11 | 2015-12-28 14:19 | 2015-12-28 14:28 | FIT-401 | Value of FIT-401 above 1 | Set value of FIT-401 as 0 | No | UV shutdown; P-501 turns off;
13 | 2015-12-29 11:11 | 2015-12-29 11:15 | MV-304 | MV-304 is open | Close MV-304 | Yes | Halt of stage 3 because change in the backwash process | UF Startup did not stop because MV-304 was closed late
14 | 2015-12-29 11:36 | 2015-12-29 11:43 | MV-303 | MV-303 is closed | Do not let MV-303 open | Yes | Halt of stage 3 because change in the backwash process | Attack Failed because Startup sequence did not start because Tank 301 was already full
16 | 2015-12-29 11:57 | 2015-12-29 12:02 | LIT-301 | Water level between L and H | Decrease water level by 1mm each second | No | Tank Overflow
17 | 2015-12-29 14:38 | 2015-12-29 14:50 | MV-303 | Closed | Do not let MV-303 open | Yes | Halt of stage 3 because change in the backwash process
19 | 2015-12-29 18:11 | 2015-12-29 18:15 | AIT-504 | Value of AIT-504 <15 uS/cm | Set value of AIT-504 to 16 uS/cm | No | RO shut down sequence starts after 30 minutes. Water should go to drain. | RO did not shutdown; Water did not go to drain
20 | 2015-12-29 18:16 | 2015-12-29 18:22 | AIT-504 | Value of AIT-504 <15 uS/cm | Set value of AIT-504 to 255 uS/cm | No | RO shut down sequence starts after 30 minutes. Water should go to drain. | RO did not shutdown; Water did not go to drain
21 | 2015-12-29 18:30 | 2015-12-29 18:42 | MV-101, LIT-101 | MV-101 is open; LIT-101 between L and H | Keep MV-101 on countinuosly; Value of LIT-101 set as 700 mm | Yes | Tank overflow
22 | 2015-12-29 22:55 | 2015-12-29 23:03 | UV-401, AIT-502, P-501 | UV-01 is on; AIT-502 is <150; P-501 is open | Stop UV-401; Value of AIT502 set as 150; Force P-501 to remain on | Yes | Possible damage to RO | P501 could not be kept on; Reduced output at FIT-502
23 | 2015-12-30 01:43 | 2015-12-30 01:54 | P-602, DPIT-301, MV-302 | DPIT-301 is <0.4 bar; MV-302 is on; P-602 is closed | Value of DPIT-301 set to >0.4 bar; Keep MV-302 open; Keep P-602 closed | Yes | System freeze
24 | 2015-12-30 09:51 | 2015-12-30 09:56 | P-203, P-205 | P-203 is on; P-205 is on | Turn of P-203 and P-205 | Yes | Change in water quality | Not much impact made due to closure of P-101 because tank T-101 became full
25 | 2015-12-30 10:02 | 2015-12-30 10:12 | LIT-401, P-401 | Value of LIT-401 <1000; P-402 is on | Set value of LIT-401 as 1000; P402 is kept on | Yes | Tank underflow
26 | 2015-12-30 17:05 | 2015-12-30 17:29 | P-101, LIT-301 | P-101 is off; P-102 is on; LIT-301 is between L and H | P-101 is turned on continuosly; Set value of LIT-301 as 801 mm | Yes | Tank 101 underflow; Tank 301 overflow
27 | 2015-12-31 01:17 | 2015-12-31 01:45 | P-302, LIT-401 | P302 is on, LIT401 Is between L and H | Keep P-302 on contineoulsy; Value of LIT401 set as 600 mm till 1:26:01 | Yes | Tank overflow
28 | 2015-12-31 01:45 | 2015-12-31 11:15 | P-302 | P302 is on | Close P-302 | Yes | Stop inflow of tank T-401
29 | 2015-12-31 15:32 | 2015-12-31 15:34 | P-201, P-203, P-205 | P-201 is closed; P-203 is closed; P-205 is closed | Turn on P-201; Turn on P-203; Turn on P-205 | Yes | Wastage of chemicals | The three dosing pump did not start because of some mechanical interlock
30 | 2015-12-31 15:48 | 2015-12-31 16:07 | LIT-101, P-101, MV-201 | P-101 is off; MV-101 is off; MV-201 is off; LIT-101 is between L and H; LIT-301 is between L and H | Turn P-101 on continuously; Turn MV-101 on continuously; Set value of LIT-101 as 700 mm; P-102 started itself because LIT301 level became low | Yes | Tank 101 underflow; Tank 301 overflow
31 | 2015-12-31 22:06 | 2015-12-31 22:12 | LIT-401 | Water level between L and H | Set LIT-401 to less than L | No | Tank overflow
32 | 2016-01-01 10:36 | 2016-01-01 10:46 | LIT-301 | Water level between L and H | Set LIT-301 to above HH | No | Tank underflow; Damage P-302
33 | 2016-01-01 14:21 | 2016-01-01 14:29 | LIT-101 | Water level between L and H | Set LIT-101 to above H | No | Tank underflow; Damage P-101
34 | 2016-01-01 17:13 | 2016-01-01 17:14 | P-101 | P-101 is on | Turn P-101 off | Yes | Stops outflow | Outflow did not stop because the system turned on P-102
35 | 2016-01-01 17:19 | 2016-01-01 17:27 | P-101, P-102 | P-101 is on; P-102 is off | Turn P-101 off; Keep P-102 off | Yes | Stops outflow
36 | 2016-01-01 22:16 | 2016-01-01 22:25 | LIT-101 | Water level between L and H | Set LIT-101 to less than LL | No | Tank overflow
37 | 2016-01-02 11:17 | 2016-01-02 11:25 | P-501, FIT-502 | P-501 is on; FIT-502 in normal range | Close P-501; Set value of FIT-502 to 1.29 at 11:18:36 | No | Reduced output | P-501 did not turn off; FIT-502 decreased to 0.8; Speed of P-501 increased to 28.50 Hz from 10 Hz during attack.
38 | 2016-01-02 11:32 | 2016-01-02 11:36 | AIT-402, AIT-502 | In Normal Range | Set value of AIT402 as 260; Set value of AIT502 to 260 | No | Water goes to drain because of overdosing | Water did not go to the drain
39 | 2016-01-02 11:44 | 2016-01-02 11:50 | FIT-401, AIT-502 | In Normal Range | Set value of FIT-401 as 0.5; Set value of AIT-502 as 140 mV | No | UV will shut down and water will go to RO | UV did not shutdown
40 | 2016-01-02 11:52 | 2016-01-02 11:57 | FIT-401 | In Normal Range | Set value of FIT-401 as 0 | No | UV will shut down and water will go to RO | P-402 did not close, both should be interlinked
41 | 2016-01-02 13:13 | 2016-01-02 13:41 | LIT-301 | Water level between L and H | decrease value by 0.5 mm per second | No | Tank overflow | Rate of decrease in water level reduced after 1:33:25 PM